| Council Sewage Spill Notification Form to the PHS |
| --- |
| Notifier | Mike Davies | TLA | Marlborough District Council |
| Date Notified | 19/06/2020 | Time Notified | 1500hrs |
| Date of Spill | 19/06/2020 | Time discovered | 0054hrs |
| Phone ( | 03 520 7400 | Phone |  | 0274 403305 |
| Location and Cause: Surrey St Picton SPS- Heavy Rainfall Event & Pump Control Issues |
| CRM No. WO050981 |
| Picton had received 55 mm of rainfall to midnight 18th June with a further 7mm to 0300hrs 19th June. Surrey St sewer pump station had issue with the pump control that meant the wet well went into overflow at 0054hrs-0137hrs. We estimate that during this period 230m³ of highly diluted wastewater was discharge to the overflow outfall. Low tide for Picton was at 0117hrs with high tide at 0735hrs. Council contractors for Picton have checked the area of overflow earlier this morning prior to the next low tide at 1301hrs. No evidence of objectionable material was found to be present on inspection. |
| Estimated Quantity | 230m3 | Estimated Duration | 43 mins | Ongoing (delete one) |  | N |
| Weather (delete one) | wet |  |
| Tide conditions at START of spill (delete one) | ebb |  |
| Is it a contact recreation area? (delete one) (Swimming, windsurfing, water skiing, paddle boarding, surfing etc.) | Yes Seasonal |  |
| Is it a recreational shellfish collection area? (delete one) | yes |  |
| Is sampling proposed? (delete one) |  | no |
| Are warning signs proposed (delete one) |  | no |
| Is a Public Health Advisory proposed (delete one) (A Council media statement that advises the public to avoid contact or take shell fish for human consumption from a recreational water area, due to a sewage spill) |  | no |

Summary of any risk mitigation action to be taken by Council

Issues are being investigated to ensure pump control does not fail. Council has engaged Streat Control who programmed the PLC for the site to look for errors in the coding. Given tidal conditions with second high tide being at 2035hrs no clear up is required.